## Technical specification
EARLY DETECTION OF BATTERY THERMAL RUNAWAY EVENTS IN ELECTRIC VEHICLE CHARGING AREAS

# System description:

The early detection system for battery thermal runaway events in electric vehicle charging areas consists of an S.Vx electronic alarm and monitoring control panel, together with multiple addressable D.CAN gas detectors, remotely installed to specifically monitor charging zones.

The S.Vx control panel and D.CAN detectors are compatible with the addressable CAN Bus system (Control Area Network). This communication network enables the integration of a large number of addressable devices within a modular installation while reducing wiring. All modules are connected via a serial two-wire bus carrying the digital communication of the entire system.

This installation enables the early detection of gases characteristic of lithium-ion battery off-gassing phenomena, such as DMC (Dimethyl Carbonate) and EMC (Ethyl Methyl Carbonate), as well as hydrogen and various hydrocarbons.

Detecting these gases at an early stage makes it possible to identify potential failure before critical conditions occur, unlike systems based solely on smoke detection.

Early detection of lithium-ion off-gassing is only effective if these gas emissions occur in sufficient concentration in the vicinity of the detector. This system does not replace a conventional fire detection.

# Positioning:

- in the immediate vicinity of charging stations

- in the immediate vicinity of charging spaces
(1 meter or less, one detector per 2 charging points)

- in areas with a high density of electric vehicles

- in the low position: 15 to 30cm from the ground

# Control actions:

Single detection threshold with:

- shutdown of charging stations

- transmission of fire risk warning

- activation of visual and audible alarm signals

# Characteristics of addressable D.CAN MPS detectors:

| Detected gases: | DMC, EMC, H₂ and hydrocarbons |
| --- | --- |
| Application: | Early detection of Li-ion battery off-gassing |
| Principle: | MPS flammable gas classification sensor |
| Function: | Early-stage detection before critical failure |
| Adjustable alarm thresholds: | A1 = 10%LEL (instantaneous) A2-A4 : unused |
| Response time (T90): | < 20 s |
| Status indication: | Normal, alarm or fault via multicolor LED |
| Output signal: | Digital – CAN Bus |
| Power supply: | 24 VDC |
| Connection method: | 4 wires (CAN Bus) |
| Connection cable: | Two twisted pairs with shielding; conductor cross-section 0.75 mm² |
| Brand: | Dalemans |

## Characteristics of S.Vx alarm control unit:

| Input types: | Serial – CAN Bus |
| --- | --- |
| Minimum number of inputs: | Depending on number of detectors |
| Maximum number of inputs: | 240 |
| Display: | Touchscreen and LED indicators |
| Alarms: | 4 programmable thresholds |
| Fault: | 1 threshold |
| Outputs |  |
| Type: | Relay with potential-free changeover contact |
| Breaking capacity: | Max. 3A – 230 VAC |
| Number of relays: | 6 programmable + 1 fault relay |
| Alarm indicators : | Internal buzzer |
|  | Color coded LEDs on the front panel |
|  | Touchscreen display |
|  | Active siren output 24V – 200mA |
| Programming: | Software in Windows environment |
| Power supply: | 230 VAC – 50 Hz |
| Standby autonomy: | 6 hours via batteries |
| Batteries charging : | 27.6V DC – 1.5A |
| Enclosure : | Metal IP55 |
| Other functions : | Manual / automatic reset Recording of events and/or measurements Local network connectivity (via Ethernet, Modbus, TCP) Alarm relay test function Adjustable behavior of alarm relays Protected test functions |
| Standard: | Compliant with EN 50545-1 |
| Brand: | Dalemans |

# Commissioning:

Commissioning and calibration of the system, including individual detector testing using calibration gas, shall be carried out by the manufacturer or its local representative.